|  | COLLIN COUNTY | Construction & Projects 4600 Community Ave. McKinney, Texas 75071 Phone: 972-547-5340 FAX: 972-547-5385 |
| --- | --- | --- |

To:		Commissioners’ Court

From:		Bill Burke/Director of Building Projects

Date:		May 27, 2009

Subject:	Award – Adult Detention Cluster 4 Security /Data Room Air System Upgrade

An upgrade to the air system in the Adult Detention Cluster 4 Security/Data room is a Permanent Improvement request that is in contingency status.  After investigation of the request I have found that the HVAC will not cool below 78 degrees in this room; 72 degrees is the optimal temperature for this room.  Since attempting to rebalance would take air from another area it is my recommendation to install a separate cooling system.

Therefore I am requesting Commissioners’ Court consideration and approval of Project X40102 to upgrade the air system in the Adult Detention Security/Data room.  Gulf Energy Systems will furnish and install the unit for the proposed amount of $11,680.00.

Thank you,

Bill Burke

Director of Building Projects